### HEAVY DUTY 4600CE RECESSED IMPELLER PUMP SPECIFICATION

(HORIZONTAL MOUNTED)

## PART 1, GENERAL

  - The following specification includes the supply of ___ horizontal vortex-type slurry pumping unit(s).  The design of these units shall be such that they are capable of pumping slurries, which may contain trash, stringy material, organic solids and grit without becoming clogged.

  - QUALITY ASSURANCE

- Pump(s) shall be supplied by the manufacture as specified herein or by an approved equal and shall be designed for use intended in the application described.

- Pump(s) shall be furnished with correctly sized motor, V-belt drive and drive guards and be mounted on a common base, as well as supply any other accessories as specifically called out in these specifications.  All equipment shall carry a manufacturers warranty.

- All of the pumps supplied per these specifications shall be the product of a single manufacturer.

  - PERFORMANCE

- The pumps shall be designed for continuous operation and will be operated continuously under normal service.

- OPERATION CRITERIA

|  | Capacity (GPM) | Total Dynamic Head (FT) | Max. Pump Speed (RPM) | Solids Size | Min. Suction Dia. (in.) | Min. Disch. Dia.(in.) | Min. Motor Size (HP) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Design Condition |  |  |  |  |  |  |  |
| Secondary Condition |  |  |  |  |  |  |  |

## PART 2, PRODUCTS

  - A.  PUMPS

- Manufacturers

a.    Pump(s) shall be the product of Fairbanks Nijhuis.

- Design

a.    Pump(s) shall be specifically designed to pump slurries that may contain solids, rags and grit.

b.   This vortex pump design shall be such that trash and solids do not have to pass through the impeller.  The impeller shall be recessed from the path of flow from the pump suction to pump discharge.  All flow paths shall be equal to or greater than the pump suction size.

c.  The hydraulic design of the cupped-type vortex impeller shall be such that performance is not negatively affected with the occurrence of wear.  The impeller design shall be such that as wear occurs, the length of the impeller vanes increases.  The impeller shall be made from ASTM A532, cast iron with a nominal 700 BHN.  Radial design impellers or impellers that include pump-out vanes on the rear shroud are not acceptable.

d.  A removable wear plate shall be provided which directs flow to the center of the volute from behind the impeller.  It shall be made of ASTM A532 with a nominal hardness of 700 BHN.  Bolted directly to the bearing housing shall be a separate stuffing box so that it can be easily removed.  The stuffing box shall not be integral with the wear plate.

e.  The pump casing shall be ASTM A532 material with a nominal hardness of 700 BHN.  It shall be of the radially split type design such that the impeller can be removed without disturbing the piping.

f.    The pump hydraulic curve shall slope continuously upward to shutoff.  Pumps with curves that contain a dip or dogleg are not acceptable.

g.   Slotted raised-face 125-lb. flanges shall be incorporated into the volute design.  These flanges shall be ground smooth to ensure an accurate fit with the piping.  The casing shall also include slots in which to house the bolts used to fasten the volute to the bearing housing.

- Materials of Construction

a.   Wear parts including the volute, impeller and wear plate shall be ASTM A532 material with a nominal 700 Brinell hardness.

- Bearing Housing

a.     The bearing housing material shall be ASTM A48CL-30 cast iron.

b.    A hardened shaft sleeve shall protect the shaft throughout the sealing area.  The shaft material shall be ASTM A108, Grade 4140 heat-treated steel.

c.    The double row, angular contact thrust ball bearings and the single-row radial ball bearings shall be grease lubricated.

- ALTERNATE -

- The double row, angular contact thrust ball bearings and the single-row radial ball bearings shall be oil lubricated.  Bearings shall carry a minimum B10 life of 100,000 hours at the best efficiency point.  A pressure vent plus oil fill and drain taps along with a built-in oil level sight glass shall be included with the bearing frame.

- Shaft Sealing

a.    Packing and HardMetal Sleeve.  Synthetic fiber graphite-impregnated packing and a Teflon water seal ring shall be used to seal the shaft.  An adjustable split bronze gland shall hold the packing in the gland housing.  The bearing housing shall incorporate a tapped ¾” NPT hole to which drain piping can be connected to carry off any leakage through the packing.  To prevent leakage between the shaft and sleeve, an O-ring sealed shaft sleeve shall be provided.  The sleeve shall be ASTM A276 cast steel heat treated to 450 BHN.  Stainless steel sleeves will not be acceptable.

- ALTERNATE -

b.  Mechanical Seal.  A single cartridge mechanical seal requiring no external flushing or a water flush shall be furnished in the pump.  The seal shall utilize a single high-reliability cartridge seal with tungsten carbide versus silicon carbide seal faces, Viton elastomers, and 316 stainless steel parts.  The base of the packing box shall be fitted with a SpiralTrac flow modification device to remove large solids from the gland housing and eject them behind the impeller.  Seals that utilize large open areas with the seal faces exposed to the pumpage shall not be acceptable.  A sleeve shall be provided to protect the shaft from abrasive wear and be O-ring sealed to prevent leakage between the shaft and the sleeve.  The sleeve shall be stainless steel construction of 300-350 Bhn.  Seals requiring a water or product flush may be furnished in lieu of the non-flushed seal, provided the contractor furnishes all of the external auxiliary equipment necessary for the flushing system.  This systems shall include, but not be limited to stainless steel tubing, pressure gauge, flowmeter, shutoff and isolation valves, manual throttle valve, strainer, pump, isolated water supply system, solenoid valve in a suitable enclosure, associated wiring, and modifications to the motor control center to actuate the solenoid valve.

- Horizontal Mounting with V-Belt Drives between Motor and Pump.

a.   A fabricated steel base with a minimum thickness of 3/8” shall be provided that is suitable to adequately support the weight of the pump, motor, drive and drive guard.

b.   An adjustable motor base shall be furnished whose design is such that the motor can easily be moved to accommodate appropriate tensioning of the V-belt drive.

c.   A “stationary control” variable speed drive complete with belts and sheaves shall be installed on the base with the pump and motor.  This type of drive is to provide a means to adjust speeds while the drive is not operating.

d.   An enclosed and approved metal belt guard shall be provided.

- Motor.  The motor provided shall meet NEMA standards and shall be ___________ type, _____ HP, _____ Phase, _______ Hertz, ______ Volts, _______ RPM.

- OPTIONAL TESTING -

- Tests

a.    Performance Testing

(Performance Test Option #1)

- Each pump shall be factory certified tested in accordance with the latest edition of Hydraulic Institute codes.  At least six test points shall be taken including the design condition and shutoff.  Test results shall  include capacity, head, efficiency and horsepower from shutoff to 150% of rated capacity.

(Performance Test Option #2)

- A registered Professional Engineer shall review and certify the test results prior to shipment.

(Performance Test Option #3)

- The owner or his representative shall witness the certified performance test.

b.    Hardness Testing

(Hardness Test Option #1)

- Individual hard metal castings shall be Brinell tested prior to shipment.  A minimum of two places shall be checked on each casting to verify the material conforms to ASTM A532.  These tests shall be by the ASTM Method E-10 and shall be conducted at the manufacturer’s plant.

(Hardness Test Option #2)

- A registered Professional Engineer shall review and certify the test results prior to shipment.

(Hardness Test Option #3)

- The owner or his representative shall witness the hardness testing.

- Pumps shall be manufactured by companies whose management system is registered to ISO-9001:2000.